## Central Heating Plant
Uniformat | System | Percent of Total | Cost per S.F. | Cost | Area | 12000
A1010 | Foundations | 3% | 27 | 324000 | $/SF | 900
A2010 | Basement Walls | 1% | 9 | 108000 | Cost | 10800000
A4010 | Slab-on-Grade | 5% | 45 | 540000
B1010 | Floor Construction | 3% | 27 | 324000
B1020 | Roof Construction | 4% | 36 | 432000
B1080 | Stair Construction | 0.8% | 7.2 | 86400
B2010 | Exterior Walls | 4% | 36 | 432000
B2020 | Exterior Windows | 0.3% | 2.7 | 32400
B2050 | Exterior Doors | 1.2% | 10.8 | 129600
B3010 | Roofing | 2% | 18 | 216000
B3060 | Roof Openings | 0.5% | 4.5 | 54000
C1010 | Interior Walls & Windows | 1.5% | 13.5 | 162000
C1030 | Interior Doors | 0.7% | 6.3 | 75600
C1090 | Interior Specialties | 0.3% | 2.7 | 32400
C2010 | Wall Finishes | 0.5% | 4.5 | 54000
C2030 | Floor Finishes | 0.5% | 4.5 | 54000
C2050 | Ceiling Finishes | 0.4% | 3.6 | 43200
D1010 | Elevators & Lifts | 0% | 0 | 0
D2010 | Domestic Water Distribution | 1% | 9 | 108000
D2015 | Plumbing Fixtures | 0.4% | 3.6 | 43200
D2020 | Sanitary Waste & Vent Systems | 0.8% | 7.2 | 86400
D3010 | Facility Fuel Systems | 4% | 36 | 432000
D3020 | Heating Systems | 15% | 135 | 1620000
D3030 | Cooling Systems | 3% | 27 | 324000
D3041 | HVAC Air Distribution | 5% | 45 | 540000
D3042 | HVAC Hydronic & Steam Distribution | 13% | 117 | 1404000
D3050 | Terminal & Package Units | 1.5% | 13.5 | 162000
D3080 | HVAC Controls & Instrumentation | 5% | 45 | 540000
D3090 | Other HVAC Systems & Equipment | 5.9% | 53.1 | 637200
D4010 | Fire Suppression Systems | 2% | 18 | 216000
D5010 | Electrical Service & Switchgear | 3% | 27 | 324000
D5020 | Electrical Distribution | 3.5% | 31.5 | 378000
D5030 | General Purpose Electrical Power | 2.5% | 22.5 | 270000
D5040 | Lighting | 1.8% | 16.2 | 194400
D6010 | Communications Systems | 0.7% | 6.3 | 75600
D7010 | Access Control & Intrusion Detection | 0.5% | 4.5 | 54000
D7020 | Video Surveillance | 0.5% | 4.5 | 54000
D7050 | Fire Detection & Alarm | 1.8% | 16.2 | 194400
E1040 | Detention Equipment | 0% | 0 | 0
E2010 | Fixed Furnishings | 0.4% | 3.6 | 43200
F1050 | Swimming Pool Systems | 0% | 0 | 0
Total | 41 | 100% | 900 | 10800000

## Notes
UniFormat Code | System Name | Percentage of Total | Notes
A1010 | Foundations | 3% | Heavy spread/mat footings for steel/concrete frame and major equipment loads. Overall FCA distribution confidence level: High.
A2010 | Basement Walls | 1% | Partial below-grade or retaining walls at some plants for pits, tunnels, or lower levels.
A4010 | Slab-on-Grade | 5% | Thick (8–12") reinforced slabs and pits supporting boilers, pumps, and heavy mechanical equipment.
B1010 | Floor Construction | 3% | Elevated platforms/mezzanines for galleries, control rooms, and access to overhead equipment.
B1020 | Roof Construction | 4% | Steel joists/beams and roof deck sized for suspended piping, ducts, and heavy snow loading.
B1080 | Stair Construction | 0.8% | Interior steel stairs to mezzanines, galleries, and roof access.
B2010 | Exterior Walls | 4% | CMU or concrete walls with exterior veneer providing durability, fire resistance, and noise control.
B2020 | Exterior Windows | 0.3% | Limited glazing at control rooms and offices only.
B2050 | Exterior Doors | 1.2% | Overhead equipment doors plus rated personnel and egress doors.
B3010 | Roofing | 2% | Insulated low-slope membrane or metal roofing over central plant structure.
B3060 | Roof Openings | 0.5% | Roof hatches, vents, and framed openings for large stacks and mechanical penetrations.
C1010 | Interior Walls & Windows | 1.5% | CMU/gypsum partitions for control rooms, offices, chemical rooms, and storage.
C1030 | Interior Doors | 0.7% | Rated doors to mechanical rooms, control areas, shops, and support spaces.
C1090 | Interior Specialties | 0.3% | Safety rails, guards, signage, and minor interior specialties.
C2010 | Wall Finishes | 0.5% | Sealed/painted CMU and gypsum finishes for control and occupied areas.
C2030 | Floor Finishes | 0.5% | Epoxy or sealed concrete in circulation zones, control rooms, and shops.
C2050 | Ceiling Finishes | 0.4% | Limited ACT/gypsum ceilings in offices and control rooms; most areas exposed structure.
D1010 | Elevators & Lifts | 0% | Typically absent – most central plants are single-level with stair access only.
D2010 | Domestic Water Distribution | 1% | Domestic water piping for restrooms, eyewash/showers, and make-up water to boilers/tanks.
D2015 | Plumbing Fixtures | 0.4% | Restroom fixtures, service sinks, safety showers, and eyewash stations.
D2020 | Sanitary Waste & Vent Systems | 0.8% | Sanitary drainage and vents for restrooms, floor drains, and neutralization basins.
D3010 | Facility Fuel Systems | 4% | Natural gas, oil, or propane fuel systems, tanks, and piping serving boilers and backup fuels.
D3020 | Heating Systems | 15% | Central boilers, economizers, stacks, and primary heating-plant equipment dominating plant cost.
D3030 | Cooling Systems | 3% | Limited share for plants that include some chillers or small cooling equipment; most are boiler-only.
D3041 | HVAC Air Distribution | 5% | Central ventilation, combustion air systems, exhaust fans, and duct mains serving plant spaces.
D3042 | HVAC Hydronic & Steam Distribution | 13% | Extensive hot-water/steam distribution, secondary pumps, expansion tanks, and specialties within plant and near outgoing mains.
D3050 | Terminal & Package Units | 1.5% | Unit heaters, cabinet heaters, and small terminal units serving control rooms and ancillary spaces.
D3080 | HVAC Controls & Instrumentation | 5% | BAS/PLC systems, sensors, actuators, and control networks for boilers, pumps, and plant operations.
D3090 | Other HVAC Systems & Equipment | 5.9% | Water treatment, specialized exhaust, draft fans, and other non-standard mechanical/process systems in the plant.
D4010 | Fire Suppression Systems | 2% | Sprinkler or pre-action systems protecting high-risk mechanical spaces and chemical rooms.
D5010 | Electrical Service & Switchgear | 3% | High-capacity 3-phase service, main switchgear, transformers, and generator connection equipment.
D5020 | Electrical Distribution | 3.5% | MCCs, distribution panels, feeders, and risers serving major mechanical and auxiliary loads.
D5030 | General Purpose Electrical Power | 2.5% | Branch circuits, receptacles, and local disconnects for tools, auxiliaries, and support equipment.
D5040 | Lighting | 1.8% | Industrial LED lighting, emergency lighting, and exterior fixtures for the plant.
D6010 | Communications Systems | 0.7% | Network, telecom, and SCADA communications for control and monitoring functions.
D7010 | Access Control & Intrusion Detection | 0.5% | Card access and intrusion detection at operator and service entries.
D7020 | Video Surveillance | 0.5% | CCTV coverage of entries, control areas, and exterior yard.
D7050 | Fire Detection & Alarm | 1.8% | Addressable fire alarm, detection, and notification integrated with plant shutdown and monitoring.
E1040 | Detention Equipment | 0% | Typically absent – central heating plants do not use detention-grade equipment.
E2010 | Fixed Furnishings | 0.4% | Fixed casework, workbenches, and storage in control rooms, shops, and support spaces.
F1050 | Swimming Pool Systems | 0% | Typically absent – no pool or natatorium systems associated with central heating plants.
Total | 41 | 100%