## Data Center
Uniformat | System | Percent of Total | Cost per S.F. | Cost | Floor Area (S.F.): | 16000
A1010 | Foundations | 2.9% | 23.2 | 371200 | Cost Per Square Foot: | 800
A2010 | Basement Walls | 0.5% | 4 | 64000 | Building Cost: | 12800000
A4010 | Slab-on-Grade | 4.3% | 34.4 | 550400
B1010 | Floor Construction | 1.9% | 15.2 | 243200
B1020 | Roof Construction | 2.9% | 23.2 | 371200
B1080 | Stair Construction | 0.3% | 2.4 | 38400
B2010 | Exterior Walls | 4.1% | 32.8 | 524800
B2020 | Exterior Windows | 0.2% | 1.6 | 25600
B2050 | Exterior Doors | 1% | 8 | 128000
B3010 | Roofing | 1.9% | 15.2 | 243200
B3060 | Roof Openings | 0.5% | 4 | 64000
C1010 | Interior Walls & Windows | 1.9% | 15.2 | 243200
C1030 | Interior Doors | 0.7% | 5.6 | 89600
C1090 | Interior Specialties | 0.4% | 3.2 | 51200
C2010 | Wall Finishes | 0.4% | 3.2 | 51200
C2030 | Floor Finishes | 0.6% | 4.8 | 76800
C2050 | Ceiling Finishes | 0.3% | 2.4 | 38400
D1010 | Elevators & Lifts | 0.2% | 1.6 | 25600
D2010 | Domestic Water Distribution | 0.4% | 3.2 | 51200
D2015 | Plumbing Fixtures | 0.3% | 2.4 | 38400
D2020 | Sanitary Waste & Vent | 0.4% | 3.2 | 51200
D3010 | Facility Fuel Systems | 3.4% | 27.2 | 435200
D3020 | Heating Systems | 2.4% | 19.2 | 307200
D3030 | Cooling Systems | 11.6% | 92.8 | 1484800
D3041 | HVAC Air Distribution | 5.3% | 42.4 | 678400
D3042 | Hydronic/Steam Distribution | 7.2% | 57.6 | 921600
D3050 | Terminal & Package Units | 1.7% | 13.6 | 217600
D3080 | HVAC Controls | 4.6% | 36.8 | 588800
D3090 | Other HVAC Equipment | 7.1% | 56.8 | 908800
D4010 | Fire Suppression Systems | 3.4% | 27.2 | 435200
D5010 | Electrical Service & Switchgear | 8.2% | 65.6 | 1049600
D5020 | Electrical Distribution | 9.7% | 77.6 | 1241600
D5030 | General Purpose Electrical | 2.4% | 19.2 | 307200
D5040 | Lighting | 1% | 8 | 128000
D6010 | Communications Systems | 1.7% | 13.6 | 217600
D7010 | Access Control & Intrusion | 1% | 8 | 128000
D7020 | Video Surveillance | 0.9% | 7.2 | 115200
D7050 | Fire Detection & Alarm | 1.9% | 15.2 | 243200
E1040 | Detention Equipment | 0% | 0 | 0
E2010 | Fixed Furnishings | 0.4% | 3.2 | 51200
F1050 | Swimming Pool Systems | 0% | 0 | 0
Total |  | 100% | 800 | 12800000

## Notes
UniFormat Code | System Name | Percentage of Total | Notes
A1010 | Foundations | 2.9% | Heavy footings/pads for UPS, generators, chillers.
A2010 | Basement Walls | 0.5% | Occasional partial basements/pits.
A4010 | Slab-on-Grade | 4.3% | Thick reinforced slab for mission-critical loads.
B1010 | Floor Construction | 1.9% | Limited mezzanines and raised-floor support.
B1020 | Roof Construction | 2.9% | Supports large rooftop mechanical loads.
B1080 | Stair Construction | 0.3% | Minimal; only mezzanine/service stairs.
B2010 | Exterior Walls | 4.1% | Blast-resistant precast/CMU; high-durability envelope.
B2020 | Exterior Windows | 0.2% | Nearly windowless for security/thermal stability.
B2050 | Exterior Doors | 1% | Secure, hardened entries and equipment access.
B3010 | Roofing | 1.9% | Robust insulated membrane roof with mechanical supports.
B3060 | Roof Openings | 0.5% | Curbs for AHUs, vents, generator stacks.
C1010 | Interior Walls & Windows | 1.9% | Partitions for NOC, offices, electrical rooms.
C1030 | Interior Doors | 0.7% | Rated hollow-metal doors with security hardware.
C1090 | Interior Specialties | 0.4% | Minimal signage and protective features.
C2010 | Wall Finishes | 0.4% | Painted CMU/gypsum in support spaces.
C2030 | Floor Finishes | 0.6% | Anti-static tiles; sealed concrete in equipment rooms.
C2050 | Ceiling Finishes | 0.3% | Limited ACT in offices/NOC only.
D1010 | Elevators & Lifts | 0.2% | Only in multi-level/mezzanine facilities.
D2010 | Domestic Water Distribution | 0.4% | Minimal—restrooms, safety systems, humidification.
D2015 | Plumbing Fixtures | 0.3% | Basic support fixtures only.
D2020 | Sanitary Waste & Vent | 0.4% | Drainage for restrooms and mechanical rooms.
D3010 | Facility Fuel Systems | 3.4% | Diesel storage/piping for generator farm.
D3020 | Heating Systems | 2.4% | Heating for NOC/offices and frost protection.
D3030 | Cooling Systems | 11.6% | Chillers, towers, pumps with N+1 redundancy.
D3041 | HVAC Air Distribution | 5.3% | CRAH/CRAC airflow + DOAS distribution.
D3042 | Hydronic/Steam Distribution | 7.2% | Redundant chilled-water loops and valves.
D3050 | Terminal & Package Units | 1.7% | In-row cooling, spot coolers, local units.
D3080 | HVAC Controls | 4.6% | Precision controls, BAS integration, monitoring.
D3090 | Other HVAC Equipment | 7.1% | Containment, economizers, humidification, filtration.
D4010 | Fire Suppression Systems | 3.4% | Clean-agent systems + pre-action zones.
D5010 | Electrical Service & Switchgear | 8.2% | Dual utility feeds, switchgear, SPDs.
D5020 | Electrical Distribution | 9.7% | UPS, batteries, PDUs, redundant distribution.
D5030 | General Purpose Electrical | 2.4% | Office/NOC receptacles; minimal share.
D5040 | Lighting | 1% | LED systems on UPS-backed circuits.
D6010 | Communications Systems | 1.7% | Fiber pathways, structured cabling, network backbone.
D7010 | Access Control & Intrusion | 1% | Mantraps, card access, multi-factor systems.
D7020 | Video Surveillance | 0.9% | Extensive CCTV for secure perimeter/interior.
D7050 | Fire Detection & Alarm | 1.9% | VESDA + addressable integration and alarms.
E1040 | Detention Equipment | 0% | Typically absent.
E2010 | Fixed Furnishings | 0.4% | NOC consoles, shelving, built-in storage.
F1050 | Swimming Pool Systems | 0% | Typically absent.
Total |  | 100% | 41