## Facilities Shop
Uniformat | System | Percent of Total | Cost per S.F. | Cost | Floor Area (S.F.): | 8500
A1010 | Foundations | 3.6% | 7.2 | 61200 | Cost Per Square Foot: | 200
A2010 | Basement Walls | 0% | 0 | 0 | Building Cost: | 1700000
A4010 | Slab-on-Grade | 4.6% | 9.2 | 78200
B1010 | Floor Construction | 1% | 2 | 17000
B1020 | Roof Construction | 5.1% | 10.2 | 86700
B1080 | Stair Construction | 1.5% | 3 | 25500
B2010 | Exterior Walls | 7.1% | 14.2 | 120700
B2020 | Exterior Windows | 2.1% | 4.2 | 35700
B2050 | Exterior Doors | 2.6% | 5.2 | 44200
B3010 | Roofing | 5% | 10 | 85000
B3060 | Roof Openings | 0.8% | 1.6 | 13600
C1010 | Interior Walls & Windows | 5.1% | 10.2 | 86700
C1030 | Interior Doors | 2.1% | 4.2 | 35700
C1090 | Interior Specialties | 2.1% | 4.2 | 35700
C2010 | Wall Finishes | 3.1% | 6.2 | 52700
C2030 | Floor Finishes | 2.6% | 5.2 | 44200
C2050 | Ceiling Finishes | 2% | 4 | 34000
D1010 | Elevators & Lifts | 0.3% | 0.6 | 5100
D2010 | Domestic Water Distribution | 2.6% | 5.2 | 44200
D2015 | Plumbing Fixtures | 1.8% | 3.6 | 30600
D2020 | Sanitary Waste & Vent Systems | 2.1% | 4.2 | 35700
D3010 | Facility Fuel Systems | 1% | 2 | 17000
D3020 | Heating Systems | 3.1% | 6.2 | 52700
D3030 | Cooling Systems | 0.5% | 1 | 8500
D3041 | HVAC Air Distribution | 3.8% | 7.6 | 64600
D3042 | HVAC Hydronic & Steam Distribution | 1% | 2 | 17000
D3050 | Terminal & Package Units | 4.2% | 8.4 | 71400
D3080 | HVAC Controls & Instrumentation | 2.1% | 4.2 | 35700
D3090 | Other HVAC Systems & Equipment | 3.8% | 7.6 | 64600
D4010 | Fire Suppression Systems | 2.6% | 5.2 | 44200
D5010 | Electrical Service & Switchgear | 2.6% | 5.2 | 44200
D5020 | Electrical Distribution | 3.6% | 7.2 | 61200
D5030 | General Purpose Electrical Power | 3.1% | 6.2 | 52700
D5040 | Lighting | 3.1% | 6.2 | 52700
D6010 | Communications Systems | 2.1% | 4.2 | 35700
D7010 | Access Control & Intrusion Detection | 1.5% | 3 | 25500
D7020 | Video Surveillance | 0% | 0 | 0
D7050 | Fire Detection & Alarm | 2.1% | 4.2 | 35700
E1040 | Detention Equipment | 0% | 0 | 0
E2010 | Fixed Furnishings | 2.6% | 5.2 | 44200
F1050 | Swimming Pool Systems | 0% | 0 | 0
Total |  | 100% | 200 | 1700000

## Notes
UniFormat Code | System Name | Percentage of Total | Notes
A1010 | Foundations | 3.6% | Spread and grade-beam foundations for steel frame and PEMB-style shop with high bay loads.
A2010 | Basement Walls | 0% | Typically absent – facilities shop modeled as slab-on-grade with no basement.
A4010 | Slab-on-Grade | 4.6% | Heavy-duty industrial slab with thickened sections, trench drains, and equipment pads.
B1010 | Floor Construction | 1% | Limited elevated framing for mezzanine storage or small platforms.
B1020 | Roof Construction | 5.1% | Steel joists/rigid frames and metal deck spanning large clear bays under snow loads.
B1080 | Stair Construction | 1.5% | Stairs to mezzanines and any second-story office or storage areas.
B2010 | Exterior Walls | 7.1% | Insulated metal panels with CMU/brick wainscot providing durable, impact-resistant shell.
B2020 | Exterior Windows | 2.1% | Limited storefront and windows at offices, break/training rooms, and reception.
B2050 | Exterior Doors | 2.6% | Multiple hollow-metal man doors plus overhead doors serving shop bays and yard.
B3010 | Roofing | 5% | Standing-seam metal or TPO roof with high R-value insulation for Montana climate.
B3060 | Roof Openings | 0.8% | Roof hatches and curbs for RTUs, exhaust fans, stacks, and other penetrations.
C1010 | Interior Walls & Windows | 5.1% | CMU and abuse-resistant partitions separating bays, storage, and office/support zones.
C1030 | Interior Doors | 2.1% | Hollow-metal doors with durable hardware at shops, tool rooms, and mechanical spaces.
C1090 | Interior Specialties | 2.1% | Tool cages, safety equipment cabinets, signage, guardrails, and miscellaneous specialties.
C2010 | Wall Finishes | 3.1% | Painted CMU/gypsum and FRP at wet or high-abuse areas for cleanability and durability.
C2030 | Floor Finishes | 2.6% | Epoxy/sealed concrete in shops; resilient finishes in offices and support spaces.
C2050 | Ceiling Finishes | 2% | Exposed structure in shop bays; ACT ceilings in offices, training rooms, and support areas.
D1010 | Elevators & Lifts | 0.3% | Small allowance for lift/platform where mezzanines or second-floor offices require accessibility.
D2010 | Domestic Water Distribution | 2.6% | Domestic water piping to restrooms, wash bays, janitor sinks, and break areas.
D2015 | Plumbing Fixtures | 1.8% | Service sinks, hose bibs, eyewash/showers, and public/staff restroom fixtures.
D2020 | Sanitary Waste & Vent Systems | 2.1% | DWV piping for restrooms, wash bays with oil-water separator, and floor drains.
D3010 | Facility Fuel Systems | 1% | Gas piping to unit heaters, radiant tubes, make-up air units, and any training rigs.
D3020 | Heating Systems | 3.1% | Gas-fired unit heaters and/or infrared radiant tubes as primary bay heating systems.
D3030 | Cooling Systems | 0.5% | Limited mechanical cooling for offices, break rooms, and IT/control spaces; shop bays largely heating-only.
D3041 | HVAC Air Distribution | 3.8% | Ducted supply/return for office core and DOAS/ventilation distribution to selected shop zones.
D3042 | HVAC Hydronic & Steam Distribution | 1% | Hydronic loops serving unit heaters, coils, or limited radiant/snow-melt where provided.
D3050 | Terminal & Package Units | 4.2% | RTUs, split systems, and terminal units providing zoned conditioning in offices and conditioned shop areas.
D3080 | HVAC Controls & Instrumentation | 2.1% | Local thermostats and DDC/BAS controls for heaters, MAUs, exhaust, and ventilation sequences.
D3090 | Other HVAC Systems & Equipment | 3.8% | Dedicated exhaust, dust collection fans, compressor room ventilation, and make-up air units.
D4010 | Fire Suppression Systems | 2.6% | Wet-pipe sprinklers (Ordinary Hazard Group 2) and dry/pre-action coverage in any unheated zones.
D5010 | Electrical Service & Switchgear | 2.6% | 800–1600A service entrance, main switchgear, and distribution equipment sized for shop loads.
D5020 | Electrical Distribution | 3.6% | Panelboards, feeders, and branch distribution to trade bays, wash areas, compressor room, and offices.
D5030 | General Purpose Electrical Power | 3.1% | Receptacles, welder outlets, lift power, cord reels, and equipment circuits throughout the facility.
D5040 | Lighting | 3.1% | LED high-bay lighting in shops and linear LED in offices with occupancy/daylight controls and egress lighting.
D6010 | Communications Systems | 2.1% | Data/telecom, Wi-Fi, and CMMS/parts-database drops in offices and shop work areas.
D7010 | Access Control & Intrusion Detection | 1.5% | Card access and intrusion detection at shop entries, yard gates, and select interior doors.
D7020 | Video Surveillance | 0% | Not included in base FCA profile – assumed as owner/technology scope, not part of building baseline.
D7050 | Fire Detection & Alarm | 2.1% | Addressable fire alarm with horn/strobes and gas detection where required.
E1040 | Detention Equipment | 0% | Typically absent – facilities shops do not include detention-grade security equipment.
E2010 | Fixed Furnishings | 2.6% | Built-in benches, counters, storage shelving, pallet-rack anchors, and office casework.
F1050 | Swimming Pool Systems | 0% | Typically absent – facility has no pool or natatorium systems. (Confidence: High)
Total |  | 100% | 41